Analogue Addressable Fire Alarm System

Incorporating:

- C-TEC’s XFP Fire Alarm Control Panel

- C-TEC’s BS 5839-6 Hush Buttons for Houses in Multiple Occupation

- Apollo’s Fire Detectors

Consultants Specification

CONTENTS

1	Scope of work	4

2	STANDARDS AND regulations	4

3	Fire ALARM Control panel	5

3.1	Key Features	5

3.2	Indicators	6

3.3	LCD Display	7

3.4	Controls	7

3.5	General User Functions	7

3.6	Authorised User Functions	8

3.7	Engineer Functions	8

3.8	Sounders	9

3.9	Alarm Monitoring	9

3.10	Auxiliary Inputs	10

3.11	Auxiliary Outputs	10

3.12	Fault Reporting	10

3.13	Wiring	11

3.14	Power Supply Specification	11

3.15	Mechanical Specification	11

4	Networking	12

5	Programming TOOLS	13

6	Documentation	13

7	Specification for BS 5839 Hush ButtonS	14

7.1	Scope of Work	14

7.2	Standards and Regulations	14

7.3	Key Features	14

7.4	Indicators	15

7.5	Controls	15

7.6	Operation Philosophy	15

7.7	Address Settings	16

7.8	Output Current	16

7.9	Conventional Circuits	16

7.10	Wiring	17

7.11	Power Supply Specification	17

7.12	Mechanical Specification	17

7.13	Documentation	17

8	Specification for Apollo’s Automatic Fire Detectors	18

8.1	Apollo’s XP95 Analogue Addressable Fire Detectors	18

8.2	Apollo’s Discovery Analogue Detectors with Distributed Intelligence	21

8.3	Apollo’s Specification for Special Detectors	27

8.4	Apollo’s Specification for Interfaces to Intelligent Fire Detection Systems	28

8.5	Apollo’s Specification for Sounders for Intelligent Detection Systems	31

9	Specification for Apollo’s Conventional Fire Detectors	32

9.1	Ionisation Smoke Detector	32

9.2	Optical Smoke Detector	32

9.3	Heat Detector	32

9.4	Bases	32

# Scope of work

1.1	To design, supply and install a complete 24Vdc networkable analogue addressable Fire Alarm Control System incorporating BS 5839-6 Hush Buttons for houses in multiple occupation (HMOs) and Apollo Fire Detectors.

1.2	The Fire Alarm Control Panel (FACP) shall form the central processing unit of the system; receiving and analysing signals from fire sensors, providing audible and visual information to the user, initiating automatic alarm response sequences and providing the means by which the user interacts with the system.

1.3	The FACP shall be easily configurable so as to meet the exact detection zone and output mapping requirements of the building.

1.4	The FACP shall be microprocessor based and operate under a multi-tasking software program.

1.5	The FACP shall provide comprehensive test, maintenance and commissioning functions with access to installation programming and diagnostic tools (including auto-learn loops, test outputs, one man walk-test and loop continuity tests).

# STANDARDS AND regulations

2.1	Where applicable, the FACP shall comply fully with the following British Standards and/or other nominated rules and regulations. The equipment manufacturer shall confirm compliance with the standards.

2.2	The equipment manufacturer shall be approved to BS EN ISO 9001 quality system standard for the design and manufacture of the equipment.

2.3	The FACP shall be designed to comply with the current edition of the IEE Wiring regulations (BS 7671).

2.4	The FACP shall be designed to comply with BS 5839-1: Fire detection and alarm systems for buildings (Code of practice for design, installation, commissioning and maintenance).

2.5	The FACP shall be designed to comply with the following parts of BS EN54 Fire detection and fire alarm systems:

2.5.1	BS EN54-2: Control and indicating equipment.

2.5.2	BS EN54-4: Power supply equipment.

2.6	The FACP shall be certified as being compliant with EN54 parts 2&4 by the Loss Prevention Certification Board (LPCB).

# Fire ALARM Control panel

## 3.1	Key Features

3.1.1	The FACP shall be a networkable analogue addressable panel and offer the following configuration variants:

One addressable loop, 16 fire zones, or

One addressable loop, 32 fire zones, or

Two addressable loops, 32 fire zones.

3.1.2	The FACP shall be compatible with Apollo’s XP95, Discovery and Xplorer device protocols - see section 8.

3.1.3	Each loop shall support up to 126 addressable devices using Apollo’s protocols. Loop devices shall be any combination (detectors, loop powered sounders, beacons, manual call points, modules or isolators) and be sub-divided into a maximum of 32 fire zones. The section of wiring corresponding to each zone circuit shall be protected from faults in other sections by the use of line isolator modules. The ‘loop’ shall be a two-wire circuit starting at, and returning to the same set of terminals at the FACP.

3.1.4	The FACP shall monitor the status of all devices on the addressable loops for fire, short-circuit fault, open-circuit fault, incorrect addressing, unauthorised device removal or exchange, pre-alarm condition and contaminated detector condition.

3.1.5	The system addressable loops shall be able to connect to Hush Buttons (fully compliant to
BS 5839-6) for houses in multiple occupation (HMOs) – see Section 7.

3.1.6	The FACP shall be certified by the manufacturer as being fully compliant with the Hush Button operation system.

3.1.7	In order to facilitate re-configuration and system expansion, the allocation of addresses to devices shall be independent of their physical arrangement on the loops.

3.1.8	The FACP shall be capable of interfacing to conventional detection systems by using a conventional zone-monitoring module.

3.1.9	The FACP shall be capable, via a suitable timer unit, of isolating a group of selected detectors in areas of the building where maintenance work is carried out. The detectors shall be automatically re-instated after a pre-determined time.

3.1.10	The FACP shall monitor the status of all internal connection and interfaces, including charger, battery and remote signalling functions.

3.1.11	The FACP shall be capable of providing audible and visual warnings when a weekly system test is required, as defined in the latest edition of BS 5839-1.

3.1.12	The FACP shall have the facility to connect to an RS-485 network bus and communicate with other controllers on that network - as detailed in section 4.

3.1.13	The FACP shall have provision to drive and monitor up to 8 repeater panels providing a repeat of the indications on the FACP display.

3.1.14	The FACP shall have an integral EN54-4 power supply unit providing 24Vdc - as detailed in section 3.14.

3.1.15	The FACP shall have integral RS-232 interfaces to allow connections to a PC and a printer - as detailed in section 5.

3.1.16	The FACP shall incorporate a real-time clock to enable events to be referenced against time and date. The user shall be able to change the time and date settings of the clock.

3.1.17	The FACP shall have an event log capable of storing up to the last 499 events.

3.1.18	The FACP shall incorporate an alarm counter that records the number of times the FACP has been in alarm state. This counter shall not be resettable.

3.1.19	The FACP shall incorporate a simple to operate keypad enabling users to access the various built-in functions and interact with the information displayed on the LCD. For security reasons, the FACP shall require a password code for entry to access level 2 (authorised user) and access level 3 (engineer).

## 3.2	Indicators

3.2.1	The FACP shall incorporate the following LED indicators, as a minimum:

| LED Label | LED Colour | Description |
| --- | --- | --- |
| Supply Present | Green | Lit steady to show that all power supplies are functioning correctly. |
| General Fire | Red | Flashes when there is a fire condition on any zone and goes steady when the alarm is silenced. Subsequent fire conditions shall restart the General Fire LED flashing until it is silenced again. |
| Fire Zones (1 LED per zone) | Red | One, or more of these LEDs shall flash in an alarm condition and shall go steady when silenced. |
| General Fault | Yellow | Flashes when there is a fault condition. Shall always be lit in conjunction with at least one other fault LED. |
| System Fault | Amber | Lit steady when a system error, such as a microprocessor fault, occurs. Remains lit even if the panel automatically clears the fault. |
| General Disablement | Yellow | Lit steady when one or more zones, sounders, outputs, or relays are disabled. |
| Test | Yellow | Lit steady when in walk-test mode. This LED shall NOT illuminate for any other test condition. |
| Accessed | Yellow | Lit steady when in access level 2 or 3. |
| Phased Evacuation | Yellow | Flashes when a phased evacuation is in process. |
| Power Supply Fault | Yellow | Lit steady when the power supply, or mains has failed, or the standby battery is in poor condition. |
| Sounder Status | Yellow | Flashes when a fault is detected on either of the two conventional sounder circuits, or if there is a sounder disablement anywhere on the system. |
| Delays Running | Yellow | Lit steady when there is an active but delayed alarm condition on any zone. Shall always be lit in conjunction with at least one Fire Zone LED. |

## 3.3	LCD Display

3.3.1	In addition to the LED indications detailed in section 3.2.1, the FACP shall also have an integral 2-line x 40 character, backlit, LCD alphanumeric display that acts as an operator interface. The LCD shall provide detailed information (in a textual format) and display system status for the following conditions:

Normal conditions

Fire conditions

Fault status

Pre-alarm conditions

Access levels 1, 2 & 3 menu functions.

## 3.4	Controls

3.4.1	The FACP shall incorporate the following pushbutton controls, as a minimum:

| Button Label | Description |
| --- | --- |
| More Information | Displays additional information on any fire, pre-alarm, or fault condition that appears on the panel’s LCD display. |
| Silence/Resound Sounders | Silences or resounds the system’s sounders (available at access levels 2 & 3 only). |
| Silence Internal Sounder | Silences the panel’s internal sounder. |
| Menu | Enables access to the panel’s menus. |
| Scroll Up / Down | Dependent on the status of the panel, these buttons shall: scroll vertically through any fire, pre-alarm, or fault conditions that appear on the panel’s LCD display scroll vertically through the panel’s user menus manipulate date, time and disablement settings, etc. serve as code input buttons to access levels 2 or 3. |
| Escape / Accept | Dependent on the status of the panel, these buttons shall: scroll horizontally through the panel’s user menus escape, or accept options available in the panel’s user menus serve as code input buttons to access levels 2 or 3. |
| Control Panel Reset | Resets the panel when the sounders are silenced (available at access levels 2 & 3 only). |
| Investigate | Starts the panel’s investigate timer function (available access levels 2 & 3 only). |

## 3.5	General User Functions

3.5.1	The FACP shall provide access level 1 functions (for a general user).

3.5.2	The FACP shall incorporate the following general user functions, as a minimum:

Display all fires on the system

Display all faults on the system

Display all disablements on the system

Display zones in test mode

Perform a lamp test

Display the alarm counter.

## 3.6	Authorised User Functions

3.6.1	The FACP shall provide a password code, or key, to restrict entry to access level 2 functions (for an authorised user).

3.6.2	The FACP shall incorporate the following authorised user functions, as a minimum:

All functions as listed in section 3.5.2

Set the time and date

Print/display/reset event log functions

Disable/enable detection zones

Disable/enable fire sounders

Disable/enable outputs

Disable/enable relays

Disable/enable devices

Disable/enable fault relay

Disable/enable output delays.

## 3.7	Engineer Functions

3.7.1	The FACP shall provide a password code to restrict entry to access level 3 functions (for an engineer).

3.7.2	The FACP shall incorporate the following engineer functions, as a minimum:

All disablements as listed in section 3.6.2

Disable/enable earth faults

Set up passwords

Connect to PC

Network functions

Perform a loop learn

Find new devices

Display fitted devices

Assign zone/group

Calibrate devices

Commission loops

Display calibration problems

Display duplicate addresses

Set day/night times

Perform a clean start

Monitor a point

Test device outputs

Test output sets

Test sounder groups

Test panel relays

Put detection zone(s) into walk-test mode

Blink detector LEDs

Intensive device monitor

Perform a loop test

Display the database

Display the panel’s software version and checksum

Display status of the panel’s PSU and standby battery

Display loop current.

## 3.8	Sounders

3.8.1	The FACP shall support both loop powered and conventional sounder circuits.

3.8.2	Loop powered sounders shall be line monitored for open-circuit and short-circuit faults.

3.8.3	The maximum number of loop powered sounders per loop @10mA shall be up to 40.

3.8.4	The number of programmable sounder groups shall be 16.

3.8.5	The FACP shall provide the necessary outputs to operate two independently programmable conventional sounder circuits. The maximum number of conventional sounders @20mA shall be up to 40 sounders for a One Loop 16 Zone panel, or up to 80 sounders for a One or Two Loop 32 Zone panel.

3.8.6	The conventional sounder circuits shall have an EOL allowing line monitoring for open-circuit and short-circuit faults.

3.8.7	The FACP shall be capable of providing a two-stage alarm sounder facility that can be programmed, either on a zonal basis or common system basis, to meet the requirements of the fire authority.

3.8.8	The FACP shall have the facility to change, on a per sounder zone basis, the sound output dependent upon whether the source of alarm is an automatic detector, e.g. smoke or heat, or a manual call point.

## 3.9	Alarm Monitoring

3.9.1	The FACP shall interrogate each addressable loop device.

3.9.2	The FACP shall have the ability to annunciate a pre-alarm condition designed to give the earliest possible warning of a potential fire condition without raising the full alarm condition.

3.9.3	The FACP shall have the ability to provide automatic warning that a detector has reached a level of contamination that requires it be replaced or serviced.

3.9.4	The FACP shall have the ability to display the analogue levels returned from the sensors.

## 3.10	Auxiliary Inputs

3.10.1	The FACP shall provide two programmable inputs as a minimum.

3.10.2	The auxiliary inputs shall connect to 0V to trigger volt-free, single-pole changeover contacts with a maximum switching current of 1A and a maximum switching voltage of 30Vdc.

## 3.11	Auxiliary Outputs

3.11.1	The FACP shall provide the following auxiliary outputs:

3 x programmable relays

1 x fault output

1 x 24V aux output @100mA.

3.11.2	The auxiliary output relays listed in section 3.11.1 shall be volt-free, single-pole changeover contacts with a maximum switching current of 1A and a maximum switching voltage of 30Vdc.

3.11.3	The relay outputs SHALL NOT be used for switching mains voltages.

## 3.12	Fault Reporting

3.12.1	The FACP shall monitor all critical system components. When a fault occurs on a critical part of the fire alarm system, the FACP shall respond by activating its internal sounder, illuminating the General Fault LED and other LEDs relating to the fault.

3.12.2	The FACP fault output shall also be activated (providing it has not been disabled). The active fault shall also be displayed on the LCD and provide text messages to indicate the precise location of where a fault has occurred in the system.

3.12.3	The following faults shall be reported in the manner described in sections 3.12.1 and 3.12.2:

Loop integrity fault

Detector head removal

Unconfigured device

Device missing

Addressable device failure

PSU fault

Battery fault

Mains failure

Mains fuse ruptured

Battery fuse ruptured

Sounder wiring open-circuit

Sounder wiring short-circuit

Microprocessor fault

Main control PCB fault

Earth fault.

## 3.13	Wiring

3.13.1	All wiring shall be installed in accordance with the current edition of BS 5839-1 and BS 7671 (IEE Wiring Regulations), and/or other relevant national standards.

3.13.2	Cables shall be fire-resistant screened cable, minimum size 1mm2.

3.13.3	Cable lengths shall be a maximum of 1Km per loop.

3.13.4	Connector blocks shall accept cables up to 1.5mm2.

3.13.5	The maximum allowable loop impedance (each conductor) shall be 20(.

3.13.6	The maximum cable capacitance shall be 0.27µF.

## 3.14	Power Supply Specification

3.14.1	The FACP shall operate on a mains supply voltage of:

230Va.c. +10%-15% @50/60 Hz

3.14.2	The FACP shall house an integral EN54 switch mode PSU rated @185-260Va.c., 50/60Hz and batteries required to power systems of up to 32 zones.

3.14.3	The FACP, standard power supply unit and standard repeater unit shall comply with BS EN54 part 4.

## 3.15	Mechanical Specification

3.15.1	The enclosures used to house the FACP, system power supply and repeater panel shall be of either plastic, or metal construction and shall not exceed the following overall dimensions:

Width:	440mm

Height:	280mm

Depth:	90mm.

3.15.2	The enclosures shall be capable of being surface, or semi-recessed mounted and shall come complete with cable entries, fixings, knockouts and front cover.

3.15.3	The overall weight of the FACP, standard power supply unit and standard repeater unit shall not exceed 5Kg (batteries excluded).

3.15.4	All enclosures shall have a minimum ingress protection to IP30 and require a special tool to open the front cover.

# Networking

4.1	The network protocol shall allow the interconnection of up to eight FACPs. Alternatively, the network protocol can be used to connect up to eight FACP repeaters to one non-networked FACP.

4.2	The key features of the FACPs network protocol when used for interconnecting FACPs are listed below:

4.2.1	Allow the interconnection of up to eight FACPs (any mix of One Loop 16 Zone panels and One or Two Loop, 32 Zone panels.)

4.2.2	The FACPs shall be connected using a 2-wire, RS485 network.

4.2.3	The FACP network shall be capable of being wired up to 1Km of cable.

4.2.4	Each networked FACP shall be programmed to:

Accept fires from other FACPs

Accept faults from other FACPs

Accept control actions, e.g. silence alarm sounders, control panel reset, from other FACPs

Accept disablement commands for zones, sounders and output sets from other FACPs.

4.2.5	It shall be possible to program cause and effects into local panels, dependent on which remote panel is in alarm.

4.2.6	All networked FACPs shall monitor all other FACPs for network wiring faults.

4.2.7	Fires detected on remote FACPs shall be displayed on local FACPs, including the point description of the alarms origin.

4.2.8	Faults detected on remote FACPs shall be displayed on local FACPs, including the point description of detectors.

4.2.9	The network shall support the programming of site data into remote FACPs from a PC connected at a local FACP.

4.2.10	Time and date shall be common to all FACPs on the network.

4.3	The key features of the FACPs network protocol when used for connecting FACPs repeaters are listed below:

4.3.1	Allow the connection of up to eight FACP repeaters to one non-networked FACP (any mix of 16 zone repeaters and 32 zone repeaters).

4.3.2	The FACP repeater network shall be capable of being wired up to 500m of cable.

4.3.3	Each FACP repeater shall offer the same functions and controls as the FACP.

# Programming TOOLS

5.1	The FACP shall be capable of interfacing with a PC using a bespoke Windows-based program for programming purposes and configuration updates.

5.2	The programming PC shall connect to the main FACP via an RS232 connection.

5.3	The FACP shall have an additional RS232 socket for the optional connection of a serial printer, e.g. for printing the panel’s event log.

5.4	The programming software shall include the following tools as a minimum:

Support Apollo’s devices

Transfer data between the PC and FACP

Print reports

Load default data

Edit loop summary

Zone and device naming

Alarm verification count

Loop configuration

Zone configuration

Group configuration

Set configuration

Site configuration

Cause & effect configuration

Network configuration

View event log

Fault diagnosis

Loop summary.

# Documentation

6.1	A complete set of documents describing the FACP including its installation, operating and maintenance instructions shall be provided.

6.2	The following documentation shall be provided, as a minimum:

Installation and Maintenance Instructions

User Manual and Log Book

Standby battery calculations showing FACP power requirements and formulas used to calculate power consumption.

# Specification for BS 5839 Hush ButtonS

## 7.1	Scope of Work

7.1.1	To design, supply and install Hush Buttons fully compliant with BS 5839-6.

7.1.2	The purpose of the Hush Buttons shall be to reduce the risk of false alarms, via the communal fire alarm system, in HMOs by providing reliable, fully monitored fire detection, alarm and silencing facilities.

7.1.3	Typically, one Hush Button shall be fitted in each individual HMO dwelling, complete with conventional detectors and sounders to provide occupants with a simple means of invoking two types of ‘hushed’ period - as detailed in section 7.6.

7.1.4	By providing HMO occupants with this level of control over their fire alarm systems, the Hush Buttons shall help reduce false alarms and prevent unnecessary building evacuations, system vandalism and the likelihood of a true alarm signal being ignored.

## 7.2	Standards and Regulations

7.2.1	Where applicable, the Hush Buttons shall comply fully with the following British Standards and/or other nominated rules and regulations.

7.2.2	The equipment manufacturer shall be approved to BS EN ISO 9001 quality system standard for the design and manufacture of the equipment.

7.2.3	The Hush Buttons shall be designed to comply with the current edition of the IEE Wiring regulations (BS 7671).

7.2.4	The Hush Buttons shall be designed to comply with the following parts of BS 5839 Fire detection and fire alarm systems for buildings:

7.2.5	BS 5839-1: Code of practice for design, installation, commissioning and maintenance.

7.2.6	BS 5839-6: Code of practice for the design and installation of fire detection and alarm systems in dwellings.

## 7.3	Key Features

7.3.1	The Hush Button shall be designed to be installed on an analogue addressable loop of a FACP. It shall have the ability to communicate its status back to the host fire panel for the attention of building management.

7.3.2	Typically, up to 20 Hush Buttons can be connected to one addressable loop (dependent on the host fire panel’s output current and devices connected).

7.3.3	The Hush Button shall be compatible with Apollo’s device protocols – see Section 8.

7.3.4	The Hush Button shall have a built-in loop isolator, a conventional detector circuit and a conventional sounder circuit.

7.3.5	The Hush Button shall provide each individual HMO dwelling with a two minute silence facility (to BS 5839 part 6, clause 12.2b) and a 15 minute isolate facility (to BS 5839 part 6, clause 12.2a).

7.3.6	The level of protection provided by the Hush Button in a HMO dwelling shall be BS 5839-6 (Grade A or B).

7.3.7	A general fire condition at the host fire panel shall override any silenced/isolated state at the Hush Button and immediately turn on its local sounders providing failsafe operation.

7.3.8	Operation of a manual call point inside the HMO dwelling shall immediately trigger the Hush Button’s sounder circuit and signal a general alarm condition to the host fire panel. The resistance of the call point when triggered shall be less than 400(.

7.3.9	The Hush Button shall be operable by HMO occupants whilst standing at floor level.

## 7.4	Indicators

7.4.1	The Hush Button shall incorporate the following user LED indicators, as a minimum:

| LED Label | LED Colour | Description |
| --- | --- | --- |
| Supply Present | Green | Lit steady when the unit is powered up. |
| Local Alarm | Red | Lit steady when a detector is in alarm. |
| Hushed | Yellow | Lit steady when the unit is in a ‘hushed’ state. Flashes during last 15 seconds of any ‘hushed’ period. |

7.4.2	The Hush Button shall incorporate the following on-board, internal LED indicator, as a minimum:

| LED Label | LED Colour | Description |
| --- | --- | --- |
| Fault | Yellow | Lit steady when there is an open-circuit, or short-circuit fault on a conventional detector, or sounder circuit. |

7.4.3	The Hush Button shall also have an integral beeper that shall activate for the following conditions:

When the ‘HUSH’ button is pressed

During the last 15 seconds of any ‘hushed’ period.

## 7.5	Controls

7.5.1	The Hush Button shall incorporate the following pushbutton control, as a minimum:

| Button Label | Description |
| --- | --- |
| HUSH | Provides either, two minute silence facility, or 15-minute isolate facility. |

## 7.6	Operation Philosophy

The Hush Button shall employ the following operating philosophy:

7.6.1	In its normal state, with no local alarm conditions, with power applied to the Hush Button: The Hush Button’s detector and sounder circuits shall be continually monitored for faults and the SUPPLY PRESENT LED lit.

7.6.2	In the event of a local alarm condition when a detector within the HMO dwelling has triggered: The Hush Button’s sounder circuit shall activate and any output devices connected to it shall sound.

7.6.3	If there is no one in the HMO dwelling to intervene during a local alarm condition, i.e. if the ‘HUSH’ button is NOT pressed: The local alarm sounders shall sound for a period of two minutes. If the local alarm clears within these two minutes, the Hush Button shall return to its normal state. If the local alarm is still present after two minutes, a general alarm shall be signalled to the host fire panel.

7.6.4	If the ‘HUSH’ button is pressed during a local alarm condition: A hushed period of two minutes shall commence. If the local alarm is cleared within these two minutes, the Hush Button shall return to its normal state. If the alarm doesn’t clear, 15 seconds before the hushed period is about to expire, a beeper shall sound to inform the HMO occupant that the alarm is about to be signalled to the host fire panel. If the ‘HUSH’ button is pressed again during this 15 second period, another two minute hushed period shall commence.

7.6.5	If the ‘HUSH’ button is pressed when there are no local alarms present: A hushed period of 15 minutes shall commence. During this period, power is cut to the local zone and no alarm signals from detectors shall be detected (however a manual call point shall trigger a full alarm if activated). If the ‘HUSH’ button is pressed again during this 15 minute period, power is re-applied to the local zone allowing normal signal processing to resume. 15 seconds before the 15 minute hushed period is about to expire, a beeper shall sound to inform the HMO occupant that the local zone is about to be re-powered. If the ‘HUSH’ button is pressed again during this 15 second period, another 15 minute hushed period shall commence.

7.6.6	Manual call points: If a manual call point is connected to the Hush Button’s detector circuit, its operation shall immediately trigger the Hush Button’s sounder circuit and signal a general alarm condition to the host fire panel.

7.6.7	General fire conditions: If, at any time, the host fire panel enters a general fire condition, it shall override any hushed state at the Hush Button and turn on its local sounders. Pressing the ‘HUSH’ button in a general fire alarm condition SHALL NOT silence the local alarm sounders and the HMO dwelling should be evacuated as per the designated fire management plan.

## 7.7	Address Settings

7.7.1	The Hush Button shall have on-board DIL switches fitted. These switches shall set addresses for the Hush Button enabling it to communicate with, and receive commands, from the host fire panel.

7.7.2	One address shall allow the Hush Button to be recognised as a Zone Monitor and another address shall allow it to be recognised as a Sounder Control Unit.

7.7.3	The DIL switch positions shall be set to either ‘0’ or ’1’ enabling Zone Monitor and Sounder Control Unit addresses to be allocated between 1 to 126 inclusive.

## 7.8	Output Current

7.8.1	The Hush Button’s output current shall provide the total alarm current of all devices connected to its conventional sounder circuit.

7.8.2	The output current to the conventional sounder circuit shall be selectable to either 12.5mA, 20mA or 30mA. An on-board link shall be used to adjust the setting of the output current.

## 7.9	Conventional Circuits

7.9.1	The Hush Button shall support one circuit for conventional sounders and one circuit for conventional detectors and manual call points. See section 9 for detector specifications.

7.9.2	The maximum sounder circuit load per Hush Button shall be 30mA, e.g. three sounders at 10mA each.

7.9.3	The maximum number of conventional detectors per Hush Button shall be 10.

7.9.4	The maximum number of conventional manual call points per Hush Button shall be 10. The call point shall be fitted with a resistor of less than 400(.

7.9.5	Each conventional circuit shall have an EOL allowing the Hush Button to line monitor for open-circuit and short-circuit faults.

## 7.10	Wiring

7.10.1	All wiring shall be installed in accordance with the current edition of BS 5839-1, BS 5839-6 and BS 7671 (IEE Wiring Regulations), and/or other relevant national standards.

7.10.2	The Hush Button’s conventional detector and sounder circuits shall be 2 x 2-core cables, fire-resistant, screened cable. Alternatively, 1 x 3-core cable may be used as 0 volt is common.
Note: This may be of lesser grade if it meets the requirements of the local authority.

7.10.3	The wiring terminals of the Hush Button shall accept cables up to 1.5mm2.

7.10.4	Cable lengths of the conventional detector and sounder circuits shall be a maximum of 100m.

## 7.11	Power Supply Specification

7.11.1	The Hush Button shall derive its power from the analogue loop and shall operate on a voltage of 22-40Vdc with a quiescent current of <5mA.

## 7.12	Mechanical Specification

7.12.1	The Hush Button shall be of plastic construction and shall not exceed the following overall dimensions:

Width:	144mm

Height:	84mm

Depth:	37mm.

7.12.2	The Hush Button shall mount on a standard UK 25mm double-gang back box.

## 7.13	Documentation

7.13.1	The equipment manufacturer shall provide a complete set of documents describing the Hush Button including its installation, operating and maintenance instructions.

# Specification for Apollo’s Automatic Fire Detectors

The FACP shall be fully compliant with Apollo’s XP95, Discovery and Xplorer device protocols.

## 8.1	Apollo’s XP95 Analogue Addressable Fire Detectors

8.1.1	Ionisation Smoke Detectors

The ionisation smoke detectors shall be suitable for detecting invisible products of combustion as well as visible smoke and be of the dual chamber single-sided source type to provide good stability in changing environmental conditions.

The radioactive source shall be Americium 241 mounted in such a way that it is mechanically secure. The device shall have been certified by the National Radiological Protection Board, or a similar body.

The detectors shall be suitable for connecting to a two-wire 24V central system and operate satisfactorily within the supply voltage range of 17V to 28Vdc.

A red indicator LED shall be provided on the detector which illuminates when the detector has reached a pre-set alarm level. The indicator shall be operated independently of the detector from the FACP.

Provision shall be made for an output from the detector suitable for operating a remote indicator or other device with a current limitation of 4 milliamps. The output shall be operated independently of the smoke detector from the FACP.

The detector shall be capable of operating within the following environmental limits:

temperature operating range (no condensation): –20ºC to +60ºC

humidity operating range: 0% to 95%RH

wind speeds: up to 10 metres per second without false alarming, or fault conditions

atmospheric pressure: equivalent to 2000m above sea level.

Separate mounting bases shall be required which enable ready removal of the detectors for maintenance. The bases shall be fitted with dual finger stainless steel contacts.

The construction of the detector and bases shall be in white, self-extinguishing polycarbonate plastic. All circuitry shall be protected against moisture and fungus. Smoke entry points shall be protected against dust and insect ingress by corrosion resistant gauze. The detectors shall be unobtrusive when installed, having a dimension not exceeding 50mm x 100mm diameter maximum, including the mounting base.

The detector shall incorporate a feature enabling it to be locked securely to its base.

Data transmissions to and from the FACP from the detector shall be via communications circuitry which is factory fitted to the detector by the original detector manufacturer and forms a complete and integral part of the detector.

The detector shall be supplied complete, fully tested and calibrated.

The unique address of the detector shall be set by the installer by means of a coded plastic card fitted to the detector base.

The detector shall be capable of being remotely tested from the FACP by the transmission of an output command bit to the addressed detector. This shall result in a healthy detector transmitting back an analogue value in excess of the recommended fire alarm threshold. The FACP shall recognize this as a test signal and shall not raise an alarm against this signal.

8.1.2	Photoelectric (Optical) Smoke Detectors

The photoelectric (optical) smoke detectors shall be suitable for detecting visible smoke such as is produced by slow smouldering fires including burning PVC. They shall be of the light scattering type using a pulsed internal LED light source and a photo-diode sensor.

The detectors shall be suitable for connecting to a 24V central system and operate satisfactorily within the supply voltage range of 17V to 28Vdc.

A clear indicator LED shall be provided on the detector which illuminates red when the detector has reached a pre-set alarm level. The indicator shall be operated independently of the detector from the FACP.

Provision shall be made for an output from the detector suitable for operating a remote indicator, or other device with a current limitation of 4 milliamps. The output shall be operated independently of the smoke detector from FACP.

The detector shall be capable of operating within the following environmental limits:

temperature operating range (no condensation): –20ºC to +60ºC

humidity operating range: 0% to 95%RH

wind speeds: not affected.

Separate mounting bases shall be required which enable ready removal of the detectors for maintenance. The bases shall be fitted with dual finger stainless steel contacts.

The construction of the detector and bases shall be in white, self-extinguishing polycarbonate plastic. All circuitry shall be protected against moisture and fungus. Smoke entry points shall be protected against dust and insect ingress by corrosion resistant gauze. The optical chamber shall be of conductive plastic and have a snap-lock fit for ease of removal when cleaning. The detectors shall be unobtrusive when installed, having a dimension not exceeding 50mm x 100mm diameter maximum, including the mounting base.

The detector shall incorporate a feature enabling it to be locked securely to its base.

Data transmissions to and from the FACP from the detector shall be via communications circuitry which is factory fitted to the detector by the original detector manufacturer and forms a complete and integral part of the detector. The detector shall be supplied complete, fully tested and calibrated.

The unique address of the detector shall be set by the installer by means of a coded plastic card fitted to the detector base.

The detector shall be capable of being remotely tested from the FACP by the transmission of an output command bit to the addressed detector. This shall result in a healthy detector transmitting back an analogue value in excess of the recommended fire alarm threshold. The FACP shall recognize this as a test signal and shall not raise an alarm against this signal.

8.1.3	Recommended Specification for Heat Detectors

The heat detector shall be electronic in operation and suitable for connecting to a 24V central system which can operate within the voltage range of 17V to 28Vdc.

The device shall detect temperature by means of an NTC thermistor.

A red indicator LED shall be provided on the detector which illuminates when the detector has reached a pre-set alarm level. The indicator shall be operated independently of the detector from the FACP.

Provision shall be made for an output from the detector suitable for operating a remote indicator or other device with a current limitation of 4 milliamps. The output shall be operated independently of the heat detector from the FACP.

The detector shall be capable of operating within the following environmental limits:

temperature operating range (no condensation): –20ºC to +60ºC

humidity operating range: 0% to 95%RH

wind speeds: not affected.

Separate mounting bases shall be required which enable ready removal of the detectors for maintenance. The bases shall be fitted with dual finger stainless steel contacts.

The construction of the detector and bases shall be in white, self-extinguishing polycarbonate plastic. Full circuitry shall be protected against moisture and fungus. The detectors shall be unobtrusive when installed, having a dimension not exceeding 50mm x 100mm diameter maximum, including the mounting base.

The detector shall incorporate a feature enabling it to be locked securely to its base.

Data transmissions to and from the FACP from the detector shall be via communications circuitry which is factory fitted to the detector by the original detector manufacturer and forms a complete and integral part of the detector.

The detector shall be supplied complete and fully tested and calibrated.

The unique address of the detector shall be set by the installer by means of a coded plastic card fitted to the detector base.

The detector shall be capable of being remotely tested from the FACP by the transmission of an output command bit to the addressed detector. This shall result in a healthy detector transmitting an analogue value in excess of the recommended fire alarm threshold. The FACP shall recognize this as a test signal and shall not raise an alarm against this signal.

8.1.4	Additional Specifications for Multi-Sensor Detectors

The following specifications are in addition to the common specifications of detectors and apply to multi-sensor detectors only.

Multi-sensor detectors shall be analogue addressable, suitable for detection of visible products of combustion (smoke) and have a fixed temperature threshold of class A2S.

The detector shall be capable of being remotely tested from the FACP by the transmission of an output command bit to the addressed detector. This shall result in a healthy detector transmitting an analogue value in excess of the recommended fire alarm threshold. The FACP shall recognize this as a test signal and shall not raise an alarm against this signal.

8.1.5	Recommended Specification for Manual Call Points (Addressable)

The call point shall be manufactured from self-extinguishing red plastic.

The overall size of the call point shall not exceed 87mm x 87mm x 52mm.

The call point shall be based upon a standard product manufactured by a reputable call point manufacturer. The manual call point shall then be modified by the manufacturer of the heat and smoke detectors to incorporate a communications module within the call point. No external alterations to the call point shall be made other than the fixing of a flush mounted LED to be located to the left of the word ‘Fire’ which shall appear in black letters across the top of the call point on the vertical face. The LED shall be red in colour.

The LED shall illuminate when the manual call point is activated. However, the illumination of the LED shall be by command from the FACP.

## 8.2	Apollo’s Discovery Analogue Detectors with Distributed Intelligence

8.2.1	Specification of Detector Common Properties

Detectors shall comply with and be type certified to EN54 (1997), Part 7 for smoke detectors and Part 5 for heat detectors.

Detectors shall be designed to be connected to a 24V (nominal) DC supply and shall operate satisfactorily within a voltage range of 14 to 28Vdc.

Detectors shall have five response modes which cover a range of sensitivities and response times. The mode for each individual detector shall be set via the FACP during a polling cycle of the communication protocol. The response mode of any detector may be changed via the FACP at any time.

Communication between detectors and the FACP shall be provided by a digital protocol on two wires as used to supply DC power to the detectors. Communication from the detectors to the FACP shall be in the form of digital response superimposed on the DC supply.

All circuits used in data communication shall be designed and manufactured by the original equipment manufacturer and shall be a complete and integral part of the detector.

Detectors shall be able to flash their LEDs each time they are polled.

If, within one second of last being polled by the FACP a detector reaches its own predetermined fire threshold the detector shall place an alarm flag and its own address on the data stream to facilitate location by the FACP.

Each detector shall have a non-volatile memory which shall be capable of being written to and read from by the FACP, using the communication protocol. The memory shall contain information and control data in the form of 8-bit bytes.

Read-only information bytes shall include fixed parameters (type code, month of manufacture of the device, approval data) and variable parameters (drift data and drift flag).

Control bytes, which the FACP can write to and read from, shall include a rapid compensation facility byte and a sensitivity setting byte controlling the LED flashing control bit.

Four, eight-bit bytes shall be provided for user data which can be written to and read by the FACP. Such data could be test dates, servicing dates, site or location codes, etc.

Detectors shall be capable of generating an alarm signal in the event of communication protocol failure (but not loss of power). This alarm shall be a 500µS current pulse with a mark/space ratio of 1:3 and shall be generated continuously for the duration of the alarm condition.

Each detector shall have its own mounting base which, with the exception of isolating bases and sounder bases, shall not contain any electronic components. Detectors shall be capable of being locked into the mounting bases to avoid unauthorised removal of the detector.

The loop address of detectors shall be set by inserting a coded plastic card into each mounting base, allowing up to a maximum of 126 unique address codes. The address shall be a simple seven bit binary code, set at the time of commissioning. The detector address card shall be held in the base so that it cannot be accidentally removed with the detector. Each address card shall provide a space visible from below when the detector is in place. The loop number and individual address or any other information can be written in the space.

Two alarm LEDs shall be provided on each detector enabling 360° visibility. The LEDs shall be controlled by the FACP, independently of the device. LEDs shall be capable of being reset by the FACP without removing power from the loop.

Provision shall be made for an output from each detector such that a remote indicator with a current limitation of 4mA@5Vdc may be operated. Switching of the remote indicator shall be independent of the detector and shall be controlled by the FACP.

Detectors shall be capable of being remotely tested from the FACP by transmission of a single bit in the communication protocol. Detectors shall respond by providing an analogue value in excess of the recommended fire threshold to indicate a healthy condition. The FACP shall recognise this response as a test signal and shall not raise a general alarm.

Detector housings shall be moulded in pure white, self-extinguishing polycarbonate, V-O rated to UL94. Detectors shall be unobtrusive when installed.

8.2.2	Additional Specifications for Ionisation Smoke Detectors

The following specifications are in addition to the common specifications of detectors and apply to ionisation smoke detectors only.

Ionisation smoke detectors shall be analogue addressable, suitable for detection of both visible and invisible products of combustion, and shall be of the dual chamber single source type.

The radioactive source shall be of Americium 241 with an activity level not exceeding 33kBq. The source shall be mounted securely and require a special tool to permit extraction by authorised personnel. Detectors shall be type certified by the National Radiological Protection Board, or a similar body.

Ionisation smoke detectors shall be capable of operating within the following environmental parameters:

Temperature range (no condensation or icing): –20°C to +60°C

Humidity (no condensation): 0% to 95%RH

Wind speed: Up to 10m/s.

The detector shall operate at atmospheric pressure up to 2000m above sea level.

A detector shall be capable of operating in any of the following modes:

| Mode | Alarm threshold Y value | Minimum time to alarm (sec) |
| --- | --- | --- |
| 1 | 0.4 | 5 |
| 2 | 0.45 | 30 |
| 3 | 0.70 | 5 |
| 4 | 0.70 | 30 |
| 5 | 1.0 | 5 |

Smoke entry points shall be protected against ingress of dust and insects by corrosion resistant gauze.

The detector shall incorporate drift compensation algorithms, and the level of compensation be recorded in non-volatile memory. When drift compensation reaches a preset level, the detector shall set a drift compensation flag, which the FACP can identify, and initiate a visible signal to indicate that the detector is in need of service. The FACP shall, when one detector signals a drift flag, be capable of checking the non-volatile memory of other detectors to see if they are nearing a state where service is required.

8.2.3	Additional Specifications for Optical (Photoelectric) Smoke Detectors

The following specifications are in addition to the common specifications of detectors and apply to optical (photoelectric) smoke detectors only.

Optical smoke detectors shall be analogue addressable, suitable for detection of visible products of combustion, and shall be of the light scattering type using a pulsed internal infra-red LED and a silicon photodiode receiver.

The optical sensing chamber shall be configured such that the horizontal optical bench housing the LED emitter and sensor is arranged radially to detect forward scattered light.

Optical smoke detectors shall be capable of operating within the following environmental parameters:

Temperature range (no condensation or icing): –20°C to +60°C

Humidity (no condensation): 0% to 95%RH

Wind speed: No effect

Atmospheric pressure: No effect.

A detector shall be capable of operating in any of the following modes:

| Mode | Alarm threshold %/m | Minimum time to alarm (sec) |
| --- | --- | --- |
| 1 | 1.4 | 5 |
| 2 | 1.45 | 30 |
| 3 | 2.1 | 5 |
| 4 | 2.1 | 30 |
| 5 | 2.8 | 5 |

Smoke entry points shall be protected against ingress of dust and insects by corrosion resistant gauze.

The detector shall incorporate drift compensation algorithms, and the level of compensation be recorded in non-volatile memory. When drift compensation reaches a preset level, the detector shall set a drift compensation flag, which the FACP can identify, and initiate a visible signal to indicate that the detector is in need of service. The FACP shall, when one detector signals a drift flag, be capable of checking the non-volatile memory of other detectors to see if they are nearing a state where service is required.

8.2.4	Additional Specifications for Heat Detectors

The following specifications are in addition to the common specifications of detectors and apply to heat detectors only.

Heat detectors shall be analogue addressable, suitable for detection of rate of rise of ambient temperature and fixed temperature threshold. Detection shall be by means of a single NTC thermistor.

Heat detectors shall be capable of operating within the following environmental parameters:

Temperature range (no condensation or icing):  –20°C to +80°C

Humidity (no condensation): 0% to 95%RH

Wind speed: No effect

Atmospheric Pressure: No effect.

A detector shall be capable of operating in any of the following modes:

|  |  | Application | Static Response |
| --- | --- | --- | --- |
| Mode | Class | Temperature (oC) |
|  |  | Typical | Max | Min | Typical | Max |
| 1 | A1R | 25 | 50 | 54 | 57 | 65 |
| 2 | A2 | 25 | 50 | 54 | 61 | 70 |
| 3 | A2S | 25 | 50 | 54 | 61 | 70 |
| 4 | CR | 25 | 80 | 84 | 90 | 100 |
| 5 | CS | 25 | 80 | 84 | 90 | 100 |

8.2.5	Additional Specifications for Multi-Sensor Detectors

The following specifications are in addition to the common specifications of detectors and apply to multi-sensor detectors only.

Multi-sensor detectors shall be analogue addressable, suitable for detection of visible products of combustion (smoke), rate of rise of ambient temperature and a fixed temperature threshold. The response modes shall be controlled via the FACP.

A detector shall be capable of operating in any of the following modes:

| Mode | Smoke sensitivity (grey smoke) | Temperature sensitivity (relative) | Response type | Minimum time to alarm(s) |
| --- | --- | --- | --- | --- |
|  | % per m | % per ft |  |  |  |
| 1 | 1.1 | 0.35 | High | Multi-sensor | 20 |
| 2 | 2.1 | 0.7 | No response to heat | Optical | 30 |
| 3 | 2.8 | 0.9 | Low | Multi-sensor | 20 |
| 4 | 4.2 | 1.4 | High | Multi-sensor | 20 |
| 5 | No response to smoke | Heat A1 | 30 |

Multi-sensor detectors shall be capable of operating within the following environmental

parameters:

Temperature range (no condensation or icing):  –20°C to +60°C

Humidity (no condensation): 0% to 95%RH

Wind speed: No effect

Atmospheric pressure: No effect.

The detector shall incorporate drift compensation algorithms, and the level of compensation be recorded in non-volatile memory. When drift compensation reaches a preset level, the detector shall set a drift compensation flag, which the FACP can identify, and initiate a visible signal to indicate that the detector is in need of service. The FACP shall, when one detector signals a drift flag, be capable of checking the non-volatile memory of other detectors to see if they are nearing a state where service is required.

8.2.6	Specification for Manual Call Points (MCP)

MCPs shall be suitable for connection to a 24V (nominal) DC supply and shall operate satisfactorily within a voltage range of 14 to 28Vdc.

Communication between MCPs and the FACP shall be provided by a digital protocol on two wires as used to supply DC power to the MCP. Communication from the MCP to the FACP shall be in the form of digital response superimposed on the DC supply. All circuits used in data communication shall be designed and manufactured by the original manufacturer and shall be a complete and integral part of the MCP.

Each MCP installed on the loop shall have a unique address, set at the commissioning stage by means of a seven-segment DIL switch.

If an MCP is activated it shall place an interrupt bit in the current polling cycle and shall transmit its address as the final seven bits of the protocol, but set all other bits to 0. It shall repeat this for a further seven polling cycles and thereafter revert to normal polling response and return an analogue value of 64.

MCPs shall contain electronic circuits similar to those in detection equipment, so that the communication protocol and fast response to the alarm state of the device are monitored. The MCP housing and electronic circuits shall be supplied by the manufacturer of the detection and interface units.

A single alarm LED shall be provided on the MCP. This LED shall be controlled, independently of the device, by the FACP. MCPs shall be able to flash their LEDs each time they are polled.

MCPs shall operate within the following environmental parameters:

Temperature range (no condensation or icing): –20°C to +60°C

Humidity (no condensation): 0% to 95%RH

Wind speed: No effect

Atmospheric pressure: No effect.

MCPs shall be capable of being remotely tested from the FACP by transmission of a single bit in the communication protocol. MCPs shall respond by providing an analogue value of 64 to indicate a healthy test condition. The FACP shall recognise this response as a test signal and should not raise a general alarm. The MCP housing shall be a red plastic moulding and shall have dimensions not exceeding 87mm x 87mm x 52mm.

8.2.7	Specification for Short Circuit Isolators

Short Circuit Isolators shall be of the stand-alone type with a mounting base that is unique to the isolator, or may be incorporated into the mounting base of a detector. Isolators may also be incorporated into interfaces.

In the event of a short-circuit fault on the loop wires the isolators shall be capable of sensing the short-circuit and disconnecting the affected part of the loop within 50µs. Isolators shall operate at between 17 and 28Vdc in normal conditions. The isolators shall open and disconnect the affected part of the loop when the loop voltage falls to 14±0.4V.

The isolators on either side of the short-circuit fault shall test the integrity of that part of the loop every 4–5 seconds. If the short-circuit fault is no longer present, the affected part of the loop shall be re-connected.

The isolators shall be supplied by the supplier of the detectors and interfaces. The mouldings of the isolators, the isolator bases and isolating bases shall be of the same material as the detectors and bases.

The isolators shall be capable of operating in the following environments:

Temperature range (no condensation or icing): –20°C to +60°C

Humidity (no condensation): 0% to 95%RH

Design environment: indoor use only.

8.2.8	Specifications for Carbon Monoxide (CO) Fire Detector

The following specifications are in addition to the common specifications of detectors and apply to carbon monoxide fire detectors only.

Carbon monoxide fire detectors shall be analogue addressable, and suitable for the detection of carbon monoxide levels produced from carbon-based materials in the smouldering stage of a fire. Detection shall be means of an electro-chemical sensor, with a cell life of not less than seven years when used in a typical environment.

The carbon monoxide fire detectors detection capabilities shall be enhanced by a rate-sensitive response in all response modes. The status response from the detector shall be rate limited to remove nuisance alarms resulting from short-term high levels of CO.

Carbon monoxide fire detectors shall be capable of operating within the following environmental parameters:

Temperature (Continuous): 0°C to +50°C

Temperature (Transient): –20°C to +50°C

Humidity (no condensation or icing) Continuous: 15% to 90%RH

Humidity (no condensation or icing) Transient: 0% to 99%RH.

Response modes (selected by the FACP):

| Mode | Alarm threshold (ppm) | Minimum time to alarm (sec) |
| --- | --- | --- |
| 1 | 30 | 60 |
| 2 | 45 | 30 |
| 3 | 45 | 60 |
| 4 | 60 | 30 |
| 5 | 75 | 30 |

The sensor shall be capable of being checked for correct function by means of a FACP-activated self-test.

## 8.3	Apollo’s Specification for Special Detectors

8.3.1	Analogue Addressable Loop-powered Beam Smoke Detector

The analogue addressable beam smoke detectors shall be able to detect the presence of smoke within internal open spaces.

The analogue addressable beam smoke detectors shall be designed to provide coverage in open areas of up to 100m in length and up to 15m wide, giving an effective protection area of 1500m2. The analogue addressable beam smoke detectors shall comprise a transmitter, receiver and interface (end-to-end beam detector) or shall have the transmitter and receiver in single housing with a reflector to return the infra-red beam from the transmitter to the receiver (reflective beam detector).

The transmitter shall project a modulated beam of infra-red light to a receiver which shall convert it to an electrical signal for processing. The received signal shall be continuously analysed, and in the event of the smoke obscuring the light by a pre-selected minimum level for a period of 8 to 10 seconds, a fire alarm condition shall be activated.

The analogue addressable beam smoke detectors shall provide selectable detection smoke levels to suit different environments. These levels are to be selectable via the interface.

The analogue addressable beam detectors shall be given a unique address. The beam transmitter, receiver, and interface unit shall be capable of being powered directly from the loop wiring.

The analogue addressable beam detectors shall include Automatic Gain Control (AGC) circuitry capable of providing compensation for long-term degradation of signal strength caused by component ageing or gradual accumulation of contamination on the lenses of the detector.

The analogue addressable beam smoke detectors shall be capable of operating within these parameters:

Supply voltage: 17 to 28Vdc

Operating range: 10 to 100m

Operating temperature: –20°C to +55°C

IP rating: 50.

8.3.2	Specification for Dual-sensor Infra-red Flame Detector

The detectors shall be capable of detecting the IR (infra-red) radiation emitted by burning materials, even some non-carbonaceous materials, e.g. Hydrogen.

The detectors shall be designed to meet, or exceed the requirements of EN54 Part 10 Flame Detectors – Point Detectors.

The detectors shall have a class 1 performance as per EN54 Part 10. That is the ability to detect an n-heptane fire of 0.1m2 at 25m, or a methylated spirit fire of 0.25m2 at 25m. Also, the detector should have the ability to detect numerous potential fire sources such as:

| Liquids | Solids | Gases |
| --- | --- | --- |
| Aviation Fuels | Coal | Butane |
| Ethanol | Cotton | Fluorine |
| Methylated spirits | Grain & Feeds | Hydrogen |
| n-Heptane | Paper | Natural Gas |
| Paraffin | Refuse | Off Gas |
| Petrol (gasoline) | Wood | Propane |

The detectors shall utilise optical filters to block unnecessary signals such as from the

Sun, or tungsten filament lamps.

The detectors shall respond to the flickering radiation signals that are associated with normal flames.

The detectors shall be tolerant of window contamination from dust.

The detectors shall have a high resistance to corrosion and mechanical damage.

The electronic assembly of the detectors shall be conformally coated.

The detectors shall conform to the EMC Directive by including RFI screening and interface suppression to minimise the effects of EMI.

The detectors shall be CE marked.

The detectors shall be analogue addressable and powered via two terminals from the loop.

The detectors shall have the following features:

a red ‘Fire’ LED visible on the detector front

two terminals for connection of a remote ‘Fire’ LED

operation of internally generated IR test signals.

On interrogation, the detectors shall signal the status of an analogue value related to the current number of flame flicker pulses counted.

The detectors shall be available in a die-cast zinc alloy housings (IP65), or in a flameproof cast metal housing (IP66) Category: EExd IIC T6, Zone 1 or 2.

The detectors shall have available a two axis adjustable stainless steel mounting bracket.

The detectors shall have available a portable test device.

The detectors shall have available a stainless steel hood to minimise the effects of sunlight when installed outdoors.

## 8.4	Apollo’s Specification for Interfaces to Intelligent Fire Detection Systems

8.4.1	Output Unit

The output unit shall provide a volt-free changeover relay contact operated by command from the FACP.

The contacts of the relay output unit shall be rated at a minimum of 1A@24Vdc. The output unit shall be capable of deriving its operating power from the addressable loop.

The output unit shall provide a red LED indication that the relay has operated.

8.4.2	Switch Monitor

The switch monitor shall provide status monitoring of one or more single pole, volt-free contacts connected on a single pair of cables to the FACP.

The switch monitor shall provide the facility to monitor the input wiring for open-circuit and short-circuit and transmit the necessary fault signal to the FACP.

The switch monitor shall communicate four input states to the FACP: ‘Normal’, ‘Fault’, ‘Pre-Alarm’ and ‘Alarm’.

The switch monitor shall provide a red LED indication for an ‘Alarm’ condition and a yellow LED for a ‘Fault’.

The switch monitor shall be capable of deriving its power directly from the addressable loop.

A version with identical functionality but smaller dimensions shall be available for use where space is limited.

A version with additional functionality shall be available for use where a delay in response is required.

8.4.3	Addressable Mini Switch Monitor (Interrupt)

The mini switch monitor (interrupt) shall provide status monitoring of one or more single pole, volt-free contacts connected on a single pair of cables to the FACP.

The mini switch monitor (interrupt) shall provide the facility to monitor the input wiring for open-circuit and short-circuit and transmit the necessary fault signal to the FACP.

The mini switch monitor (interrupt) shall communicate three input states to the FACP: ‘Normal’, ‘Fault’ and ‘Alarm’.

The mini switch monitor (interrupt) shall provide a ‘priority interrupt’ where a fast response to the signal is required.

The mini switch monitor (interrupt) shall provide an integral red LED and provision for a remote LED which is switched automatically with the integral LED.

The mini switch monitor (interrupt) shall have small dimensions for use where space is limited.

8.4.4	Sounder Control Unit

The sounder control unit shall be capable of monitoring and driving a circuit of alarm sounders.

The output of the sounder control unit shall be rated at 1A.

The sounder control unit shall be capable of operating the sounders in a pulsing or continuous mode as determined by the FACP.

The sounder control unit shall provide the facility to monitor the wiring to the alarm devices for open-circuit, or short-circuit and transmit the necessary fault signal to the FACP.

The sounder control unit shall provide the facility to monitor for failure of the local power supply and transmit the necessary fault signal to the FACP.

The sounder control unit shall provide a red LED indication that the sounder circuit has been actuated. It shall also provide a yellow LED indication for any detected faults.

The sounder control unit should be capable of being addressed into a group by means of a separate 4-bit DIL switch.

The sounder control unit should have the facility for synchronising the output for continuous and pulsed operation with other addressable alarm devices.

8.4.5	Input/Output Unit

The input/output unit shall provide a volt-free changeover relay contact operated by command from the FACP.

The contacts of the input/output unit shall be rated at a minimum of 1A@24Vdc.

The input/output unit shall be capable of deriving its operating power from the addressable loop.

The input/output unit shall provide a red LED indication that the relay has operated.

The input/output unit shall provide a yellow LED to indicate a ‘Fault’ condition; open-circuit and short-circuit on the input wiring, and a red LED to indicate when the switch input is closed.

The input/output unit shall provide monitoring of the status of a single pole, volt-free contact connected on a single pair of cables, to the FACP.

The input/output unit shall provide a further opto-coupled input for monitoring an external voltage.

The input/output unit shall communicate three input states to the FACP: ‘Normal’, ‘Fault’ and ‘Switch Closed’.

8.4.6	Zone Monitor

The zone monitor shall power and control the operation of a zone of conventional smoke detectors and manual call points.

The zone monitor shall provide the facility to monitor the input wiring for open-circuit and short-circuit faults and transmit the necessary fault signal to the FACP.

The zone monitor shall provide the facility to use ‘active end-of-line devices’ and diode bases for detector head removal monitoring.

The zone monitor shall communicate three input states to the FACP: ‘Normal’, ‘Fault’ and ‘Alarm’.

The zone monitor shall provide a red LED indication for an ‘Alarm’ condition and shall latch in the ‘Alarm’ condition.

The zone monitor shall provide the facility to increase the current on the zone to enable full illumination of detector LEDs in the ‘Alarm’ state.

The zone monitor shall provide the facility to power and control intrinsically safe detectors and manual call points via a safety barrier by cutting a wire link.

The zone monitor shall be capable of deriving its power directly from the addressable loop.

8.4.7	Mains Switching Input/Output Unit

The mains switching input/output unit shall provide a single-pole, volt-free relay contact operated by command from the FACP.

The relay contact of the mains switching input/output unit shall be rated at a minimum of 5A@250Vac and 2A@48Vdc.

The mains switching input/output unit shall be capable of deriving its operating power from the addressable loop.

The mains switching input/output unit shall provide a red LED indication that the relay has operated.

The mains switching input/output unit shall provide a yellow LED to indicate a ‘Fault’ condition; open-circuit and short-circuit on the input wiring and a red LED to indicate when the switch input is closed.

The mains switching input/output unit shall provide status monitoring of one or more single pole, volt-free contacts connected on a single pair of cables to the FACP.

The mains switching input/output unit shall communicate three input states to the FACP: ‘Normal’, ‘Fault’ and ‘Switch Closed’.

## 8.5	Apollo’s Specification for Sounders for Intelligent Detection Systems

8.5.1	Intelligent Base Sounder

The addressable base sounder shall provide an output of 85dB(A) at 1 metre and shall have a low current consumption at this level.

The addressable base sounder shall have a DIL switch selectable option of changing the output to 92dB(A) at 1 metre.

The addressable base sounder shall be supplied as a sounder base only, so that a detector can be fitted, or with a cover for use as a stand-alone sounder.

The addressable base sounder shall produce either a continuous alternating tone of 0.5s 610Hz, 0.5s 510Hz or a pulsed tone of 1s 510Hz, 1s off, on command from the FACP. The addressable base sounder shall be capable of deriving its power directly from the addressable loop.

A version of the addressable base sounder shall be available with identical functionality but without a terminal block for points where an isolating base is to be used.

8.5.2	Addressable Open Area Sounder

The addressable open area sounder shall provide an output of 100dB(A) at 1 metre and have a low current consumption at this level.

The addressable open area sounder shall produce either a continuous alternating tone, or a pulsed tone on command from the FACP.

The addressable open area sounder shall have a DIL switch selectable option of changing the volume output to 92dB(A) at 1 metre. The addressable open area sounder shall be capable of deriving its power directly from the addressable loop.

The addressable open area sounder shall have the facility to be synchronised in continuous and pulsed operation with other addressable alarm devices. The addressable open area sounder shall have the facility to be addressed as part of a group by using a separate 4-bit DIL switch.

# Specification for Apollo’s Conventional Fire Detectors

The conventional detectors range shall consist of ionisation, integrating ionisation and optical smoke detectors, four grades of heat detector and a range of bases.

Each type of conventional detector shall be available in three versions:

• a standard version

• a version with an LED which flashes continuously in quiescent mode

• and one with both a flashing LED and a magnet-operated test switch (reed relay).

Conventional detectors shall be tested and approved to the following standards:

EN54-7:2000 – optical and ionisation smoke detectors

EN54-5:2000 – heat detectors.

## 9.1	Ionisation Smoke Detector

The sensing part of the detector shall consist of two chambers; an open, outer chamber and a semi-sealed reference chamber within. Mounted in the reference chamber shall be a low activity radioactive foil of Americium 241 which shall enable current to flow between the inner and outer chambers when the detector is powered up. As smoke enters the detector, it shall cause a reduction of the current flow in the outer chamber and hence an increase in voltage measured at the junction between the two chambers. The voltage increase shall be monitored by the electronic circuitry which shall trigger the detector into the alarm state at a preset threshold. An externally visible red LED shall light up when the detector changes to alarm state. An integrating ionisation detector, suitable for use in areas where transient levels of smoke may be expected, shall also be available.

## 9.2	Optical Smoke Detector

Optical smoke detectors shall incorporate a pulsing LED located in a chamber within the housing of the detector. The chamber shall be designed to exclude light from any external source. At an angle to the LED shall be a photo-diode which normally does not register the column of light emitted by the LED. In the event of smoke from a fire entering the chamber, the light pulse from the LED shall be scattered and hence registered by the photo-diode. If the photo-diode “sees” smoke on the two following pulses, the detector shall change into the alarm state and the indicator LED shall light up. The detector housing shall be identical to that of the ionisation detector but shall have an indicator LED which is clear in quiescent state but produces red light in alarm.

## 9.3	Heat Detector

The heat detectors shall operate by using a matched pair of thermistors to sense heat. One thermistor shall be exposed to the ambient temperature, the other shall be sealed. In normal conditions the two thermistors shall register similar temperatures, but, on the development of a fire, the temperature recorded by the exposed thermistor shall increase rapidly, resulting in an imbalance, causing the detector to change into the alarm state. Rate-of-rise detectors shall be designed to detect a fire as the temperature increases, but they shall also have a fixed upper limit at which the detector will go into alarm if the rate of temperature increase has been too slow to trigger the detector earlier. The (static response) heat detector shall only have one thermistor and change to the alarm state at a preset temperature. Externally, the heat detectors shall be distinguishable from the smoke detectors by having wide openings to the surrounding atmosphere to allow good movement of air around the external thermistor.

## 9.4	Bases

The bases shall be designed to enable detectors to be plugged in without any force. All bases shall be lockable. The base shall contain no electronic parts which could be damaged during installation.